## Slide 1: Insights into designing, occupying and managing an NZEB Rajan Rawal Yash Shukla Centre for Advanced Research in Building Science and Energy, CEPT University

## Slide 2
CONTEXT : India
Energy Consumption for space-cooling in India (ICAP)
135 TWh (2017-18)
600 TWh (2037-38)
Per Capita Cooling Consumption (ICAP)
272 kWh Global Average
69 kWh in India
30% of global emissions due to space cooling by 2050 as compared to 8% in 2016 (IEA)
Image Source: https://robertscribbler.com/2015/06/02/human-hothouse-death-toll-climbs-to-2300-in-india-monsoon-suppressed-delayed/
Notes: Image source: https://robertscribbler.com/2015/06/02/human-hothouse-death-toll-climbs-to-2300-in-india-monsoon-suppressed-delayed/

## Slide 3
CONTEXT : CEPT Uni, Ahmedabad
Ahmedabad - UNESCO World Heritage City
Significant place for Modern Movement in Indian Architecture
CEPT University – A habitat university
understanding,
designing,
planning,
constructing.

## Slide 4
Centre for Advanced Research
in Building Science and Energy
Centre for Advanced Research in Building Science and Energy
Research activities
Building Physics – Material Characterization
Thermal Comfort
Low Energy Cooling
Modelling and Simulation
IT in Buildings, Sensors and Control
Design – Technology - Policy

## Slide 5
Site: CEPT Campus, Hussain and Doshi Gufa

## Slide 6
CARBSE – Iterative Design Process
Predesign
  Climate Analysis
  Technical Potential Analysis
Conceptual Design
  Passive Thermal Comfort
  Building Massing
  HVAC System Options
System Development
  Section, Windows, Shading, Daylighting
  Active System Thermal Comfort
  HVAC Capacity Optimization
  Natural Ventilation Scheduling, CFD
Systems Optimization
Three in-person charrettes in Ahmedabad
Over 50 virtual meetings and presentations

## Slide 7
CARBSE – Building Massing Exercise
Basis of Design for Energy Performance

## Slide 8
Option 1
Option 2
Option 4
Option 3
CARBSE – Building Massing Exercise

## Slide 9
CARBSE – Passive Design Approach

## Slide 10
Base Case
No light shelf
(70 deg cut-off)
Option 1
500 light shelf
(39 deg cut-off)
Option 2
800 light shelf
(30 deg cut-off)
CARBSE – Sun Control : South Facing Clerestory

## Slide 11
CARBSE – UDI Analysis (>2000) on Work Plane
Reduced VT reduced UDI(>2000) by UP TO 30% !

## Slide 12
Feb Evening
Jan Morning
CARBSE – Thermal Comfort and NV Potential

## Slide 13
CARBSE – Building Information Modelling

## Slide 14
CARBSE – Net Zero Energy Building

## Slide 15
3.1 WALL SUPER STRUCTURE
u - VALUE (W/m 2)=0.42
R - VALUE (m 2.K/W)=2.38
3.2 WALL BASEMENT
u - VALUE (W/m 2)=2.01
R - VALUE (m 2.K/W)=0.50
3.3 WALL BASEMENT
u - VALUE (W/m 2)=0.28
R - VALUE (m 2.K/W)=3.59
3.4 WINDOW
u - VALUE (W/m 2)=1.70
R - VALUE (m 2.K/W)=0.588
12mm Cement
Plaster
230mm Red Brick
50mm X.P.S Insulation
110mm Red Brick
12mm Cement
Plaster
230mm Red Brick
1mm PVC Film
18mm Polymer
Plaster
12mm Cement
Plaster
3mm Aluminum
Composite Panel
18mm Plywood
100mm X.P.S Insulation
200mm R.C.C.
1mm PVC Film
18mm Polymer
Plaster
Low E Double Glass Glazing With UPVC Frame
VLT - 39%
Reflection int - 14%
External -23%
SF - 29%
SC - 0.33
U-Value - 1.790W/m 2 k
CARBSE – Wall Construction

## Slide 16
1.1 ROOF ASSEMBLY
u - VALUE (W/m2)=0.38
R - VALUE (m 2.K/W)=2.654
1.2 ROOF ASSEMBLY
u - VALUE (W/m 2)=0.38
R - VALUE (m 2.K/W)=2.654
2.1 FLOOR- First Floor
u - VALUE (W/m 2)=0.55
R - VALUE (m 2.K/W)=1.82
2.2 FLOOR- First Floor
u - VALUE (W/m 2)=0.55
R - VALUE (m 2.K/W)=1.82
2mm High SRI Paint
50mm Concrete Screed
2mm Roof Seal- Water
Proofing Membrane
3mm Geotextile Sheet
2mm High SRI Paint
50mm Concrete Screed
2mm Roof Seal- Waterproofing Membrane
25mm Kota Stone
50mm Cement Sand Bed
150mm R.C.C.
50mm X.P.S. Insulation
6mm Feweis Plaster
25mm Kota Stone
50mm Cement Sand Bed
50mm X.P.S. Insulation
150mm R.C.C.
12mm Cement Plaster
45mm Spray Foam Insulation(PUF)
150mm R.C.C.
12mm Plaster
3mm Geotextile Sheet
45mm Spray Foam Insulation(PUF)
150mm R.C.C.
12mm Plaster
CARBSE – Roof Construction

## Slide 17
CARBSE – Net Zero Energy Building
Ground Floor Plan
First Floor Plan
Transverse Section A
Longitudinal Section
Transverse Section B

## Slide 18
Hot Outdoor Environment
Comfortable Outdoor Environment
CARBSE – Net Zero Energy Building

## Slide 19
CARBSE – Net Zero Energy Building

## Slide 20
CARBSE – Net Zero Energy Building

## Slide 21
CARBSE – Net Zero Energy Building

## Slide 22
N
Vision, clerestories, lightshleves on south bring in diffuse daylight with occupant control
Stack effect design, solar chimney for natural ventilation
South facing PV panels tilted to latitude angle
Ground heat exchange
Optimized envelope: Insulated walls and roof, efficient windows with separate properties for vision and clerestory
North light for daylighting
Radiant cooling and DOAS integrates with natural ventilation
Climate controlled spaces zoned separately
Outdoor exhibit area reduces conditioned area
Lighting LPD at 4.7 w/m2 and vacancy and daylighting controls
Integrated Systems
CARBSE – Net Zero Energy Building

## Slide 23
CARBSE – Net Zero Energy Building
Promotor
Architects - Designer
Contractor
Operation and Maintenance

## Slide 24
CARBSE – Monitoring Strategies
“Every line is the perfect length if you don't measure it”
-Marty Rubin

## Slide 25
CARBSE – Monitoring Strategies
Building Information Systems
Thermal Comfort, Temp – Humidity
Visual Comfort, Light
Occupancy
Outdoor conditions
Equipment usage
Building Management Systems
Energy Management
  Energy used to maintain comfort
  Energy used for equipment

## Slide 26
CARBSE – Monitoring Strategies
Envelope
Environment
Energy
Behavior
Chiller
HVAC
VFD
Photovoltaic
Outdoor
HVAC
Lighting
Plug Loads
Photovoltaic
Operation
Comfort
Consumption
Generation
Historical
Operation
Display
Controls
Integration
Monitoring

## Slide 27
CARBSE – Monitoring Strategies
VRF
Energy Meters
Chillers
VRV Units
Digital Scrolls
Envelope
Communication Gateway
Photovoltaic
Lighting
Radiant
Chilled Plant
DOAS
Sensors and Controllers
Guarded Hot Box
Comfort Chamber
Fans
Monitoring and Integration
Controls Hardware
Building Control System

## Slide 28
Wire/Wireless
Communication
Monitoring &
Management
Computer
Communication
Gateway (LGR-
Automated Logic)
Modbus (RS485)
Energy Meters
Field
Space tier
Network
Communication
tier
Station level
management
tier
CARBSE – Monitoring Strategies
Sensor Location Example
BMS Screen shot

## Slide 29
CARBSE – Monitoring Strategies

## Slide 30
CARBSE – Monitoring Strategies

## Slide 31
CARBSE – Monitoring Strategies
Approximately 1000 points – Indoor Environment – Energy Consumption – Energy Generation – Outdoor weather conditions – End use, lighting, HVAC, Plug and Process.

## Slide 32
CARBSE – Monitoring Strategies

## Slide 33
CARBSE – Outdoor Conditions

## Slide 34
Interior and exterior surface temperatures for the window and roof – typical summer week (2018)
CARBSE – Outdoor & Indoor comparison

## Slide 35
Environment and energy-related parameters – typical summer week (2018)
CARBSE – Indoor Environment and Energy

## Slide 36
Environment and energy-related parameters – typical winter week (2018)
CARBSE – Indoor Environment and Energy

## Slide 37
Hourly space energy consumption for each day
CARBSE – Hourly Energy consumption - Annual

## Slide 38
CARBSE – Annual Energy Consumption
Chart: Monthly Consumption and Generation
| 42370 | 42401 | 42430 | 42461 | 42491 | 42522 | 42552 | 42583 | 42614 | 42644 | 42675 | 42705
Energy Consumption | 2183.8365 | 1518.6579 | 2009.8912 | 2877.8356 | 4093.7793 | 4920.1362 | 3859.3143 | 3546.6503 | 3873.0227 | 2093.1845 | 695.5848 | 728.8314
Energy Generation | -3177.6577 | -3552.121 | -4378.417 | -4108.3703 | -3744.953 | -3233.004 | -2299.2478 | -1808.5078 | -3403.9091 | -3248.5196 | -3533.4389 | -2960.0609

## Slide 39
Total daily space consumption with daily average outdoor temperature (2017-2018)
CARBSE – Outdoor Air temp with Daily Energy: Annual

## Slide 40
Variation of hourly indoor and outdoor temperatures with the mode of cooling (2017-2018)
CARBSE – Outdoor Air temp & Indoor Air Annual

## Slide 41
Energy generation, process consumption, and space consumption (2016-17) with operation and cooling loads
CARBSE – Annual Energy Consumption - EPI

## Slide 42
Energy generation, process consumption, and space consumption with operation and cooling loads
CARBSE – Annual Energy Consumption

## Slide 43
CARBSE – Occupant Comfort Surveys
Four times a week, Mondays and Thursdays, 11h00 and 16h00
Occupants have choice to raise request for adjustment anytime
Air Temp, RH, MRT, Clo. and MET at each cluster, Provision of desk level personal fans, pedestal fans.
Seven point ASHRAE Scale
  Thermal Comfort Sensation
  Thermal Comfort Satisfaction
  Thermal Comfort Preference

## Slide 44
Indoor temperature against IMAC 80% and 90% acceptability limits (2017-2018)
CARBSE – Thermal Comfort, Adaptive Model

## Slide 45
Thermal sensation and acceptability versus indoor air temperature
CARBSE – Thermal Comfort, Adaptive Model

## Slide 46
Thermal comfort versus temperature
CARBSE – Thermal Comfort, Adaptive Model

## Slide 47
CARBSE – NZEB Partners
Owens Corning
Asahi India Glass
ECOPHIT SGS – Uponor
Sashwath Clean Energy
Citizen Industries
Yogi Engineers
Volpak Systems
United Technologies - Automated Logic

## Slide 48: Thank You rajanrawal@cept.ac.in yash.Shukla@cept.ac.in